## NMIREF Form 1
NORTHERN SAMAR ELECTRIC COOPERATIVE, INC.
|  | NORSAMELCO | [16 empty] | NMIREF Form 1
Brgy. Magsaysay, Bobon, Northern Samar
Date Applied:
NET METERING and INTERCONNECTION of RENEWABLE ENERGY FACILITY (NMIREF) ASSESSMENT CHECKLIST APPLICATION
APPLICANT (Last Name, Given Name, Middle Name) | [15 empty] | DATE OF BIRTH (M/D/Y)
[18 empty] | - | -
TYPE OF MEMBERSHIP : |  |  |  | Single | Joint |  | Juridical |  |  | CIVIL STATUS: |  |  |  | Single |  |  | Married |  | Widowed |  | Others
SPOUSE (Last Name, Given Name, Middle Name) If Married
NAME OF ESTABLISHMENT / BUSINESS
LOCATION OF INSTALLATION (House Number, Street, Barangay, Town/City)
LANDMARK | [7 empty] | Consumer Contact #: | [8 empty] | - |  | -
TYPE OF APPLICATION: |  |  | NEW (Pls. provide nearest account) | [5 empty] | -
|  |  | EXISTING (Account Number) | [5 empty] | -
A. CHECKLIST / EVALUATION
[7 empty] | Requirements |  |  |  | Compliance Status | [5 empty] | Date Submitted (for Lacking Documents |  |  | Remarks
***Required Prior to Inspection | [10 empty] | Submitted |  | Lacking
From APPLICANT
| Letter of Intent | [6 empty] | ü
| Description of Proposed Connection | [6 empty] | ü
| List of Certified Equipments / Data Sheet | [6 empty] | ü
| Picture of the Plant (frontal & isometric) | [6 empty] | ü
| Detailed Planning Data (Specification) | [6 empty] | ü
| Relevant Standard Planning Data | [6 empty] | ü
| Detailed Single Line Diagram | [6 empty] | ü
| 1 Valid ID Card | [6 empty] | ü
| Barangay Certificate of Residency | [6 empty] | ü
| NMIREF Form 2 (On Site Inspection & Testing Form) | [6 empty] | ü
***Required Once On-Site Inspection & Testing Passed
From OTHER OFFICES
| BFP Safety Clearance | [6 empty] | ü
| Electrical Plan Signed by PEE | [6 empty] | ü
Others ______________________
From NORSAMELCO
| Distribution Impact Study (for 5KW above) | [6 empty] | ü
| Distribution Asset Study (for 5KW above) | [6 empty] | ü
| NMIREF Agreement | [6 empty] | ü
Pre-Membership Education Seminar
Affidavit of Waiver
Affidavit of Administratorship
Membership Form
Flying Connection Contract
| Statement of Account | [6 empty] | ü
| Others | Proof of Lot Ownership | [5 empty] | ü
Assessed / Evaluated by:
INSTITUTIONAL SERVICES DEPARTMENT | [5 empty] | TECHNICAL SERVICES DEPARTMENT | [8 empty] | CORPLAN DEPARTMENT
Date _____________ | [5 empty] | Date _____________ | [8 empty] | Date _____________
| RECOMMENDING APPROVAL: | [10 empty] | APPROVED BY:
| Engr. NILO A. ESTOPA | [10 empty] | Engr. HECTOR N. TABILISMA
| TSD Manager | [10 empty] | Acting General Manager

## NMIREF Form 2
NORTHERN SAMAR ELECTRIC COOPERATIVE, INC.
NORSAMELCO
|  | Brgy. Magsaysay, Bobon, Northern Samar | [23 empty] | NMIREF Form 2
Date Inspectioned:
NET METERING and INTERCONNECTION of RENEWABLE ENERGY FACILITY (NMIREF) ON-SITE INSPECTION & TESTING
APPLICANT (Last Name, Given Name, Middle Name)
NAME OF ESTABLISHMENT / BUSINESS
LOCATION OF INSTALLATION (House Number, Street, Barangay, Town/City)
LANDMARK
PLANT GEOGRAPHICAL LOCATION | [11 empty] | INSPECTION FEE PAYMENT DETAILS: | [5 empty] | Amount: ________________________________________
LAT |  |  |  | LONG | [13 empty] | OR #: ________________________ | [5 empty] | Date Paid: ______________
SERVICE CLASSIFICATION: |  |  | Residential |  |  |  |  | Low Voltage | [5 empty] | High Voltage
[6 empty] | Commercial | [5 empty] | St. Light |  |  |  | Gov't. Building |  |  |  |  | Industrial |  |  |  |  | Special Lighting
[6 empty] | Religiuos Institution | [5 empty] | Cemetery |  |  |  | School Building |  |  |  |  | Water System |  |  |  |  | Others ____________
TYPE OF R.E. TECHNOLOGY: |  |  |  |  | Solar (Photovoltaic) | [6 empty] | Wind |  |  |  | Biomass / Biogas | [5 empty] | Others : (Pls. Specify)
GENERATOR TYPE: |  |  |  |  | Inverter | [6 empty] | Synchronous | [6 empty] | Induction
LOT OWNERSHIP: |  |  |  |  | Owned | [6 empty] | Tenant | [6 empty] | Government Lot
BUILDING OWNERSHIP: |  |  |  |  | Owned | [6 empty] | Tenant | [6 empty] | Government Building
BUILDING STRUCTURE: |  |  |  |  | Light Materials | [6 empty] | Concrete Materials | [6 empty] | Semi Light / Concrete Materials
A. GENERAL PLANT INFORMATION (AS INSPECTED) :
Plant KW Rating: | [9 empty] | Voltage Rating (Volts): | [10 empty] | Power Factor :
Plant KVA Rating: | [9 empty] | Current Rating (Amps): | [10 empty] | Efficiency:
Phases: |  |  | 3-Phase/4-wire | [6 empty] | 3-Phase/3-wire | [7 empty] | V-Phase | [5 empty] | 1-Phase
Grounding: |  |  | System | [6 empty] | Equipment | [7 empty] | Others: (Pls. Specify)
Maximum Symmetrical Faults: |  |  |  |  | 3Phase Fault: | [7 empty] | Line-to-Line Fault: | [9 empty] | SLG Fault:
Number of Generating Units:
Rated Capacity of Each Unit: | [6 empty] | KW |  | Gross KW: | [9 empty] | Gross KW:
[7 empty] | KVA |  | Gross KVA: | [9 empty] | Gross KVA:
|  |  |  | AC Net Capacity |  |  |  |  | KW: | [9 empty] | KW:
B. PLANT EQUIPMENT DATA CHECKLIST (AS INSPECTED) :
Visible Disconect Device? | [9 empty] | Yes |  | No |  |  |  | Synchronizing Device? | [9 empty] | Yes |  |  | No
Anti-Islanding Protection? | [9 empty] | Yes |  | No |  |  |  | Automatic Reclosing Capability? | [9 empty] | Yes |  |  | No
Under/Over Voltage Check Relay? | [9 empty] | Yes |  | No |  |  |  | Under/Over Frequency Relay? | [9 empty] | Yes |  |  | No
Synchronism Check Relay: | [9 empty] | Yes |  | No |  |  |  | Overvoltage Restrained Relay? | [9 empty] | Yes |  |  | No
With Ammeter/Voltmeter/Wattmeter? | [9 empty] | Yes |  | No |  |  |  | Overcurrent Restrained Relay? | [9 empty] | Yes |  |  | No
C. PHOTO VOLTAIC / SOLAR PANEL MODULE DATA (ACTUAL AS INSPECTED) :
Manufacturer : | [9 empty] | Type : | [10 empty] | Model No. :
Rated Output : | [9 empty] | Rated Current : | [10 empty] | Open Circuit Voltage :
No. of Units : | [9 empty] | Rated Voltage : | [10 empty] | Short Circuit Current :
D. SOLAR PANEL INVERTER DATA (ACTUAL AS INSPECTED) :
Manufacturer : | [9 empty] | Model No. : | [12 empty] | Grid-Tied |  |  |  |  | Off-Grid
Rated Capacity : | [9 empty] | No. Of Units : | [11 empty] | No. of Phases :
Rated Power Factor : | [9 empty] | Output Frequency : | [11 empty] | Total Harmonic Distortion:
Efficiency : | [9 empty] | DC Input Current : | [11 empty] | DC Injected Current :
DC Input Voltage : | [9 empty] | AC Output Current :
AC Output Voltage : | [9 empty] | Output Waveform : |  |  |  |  | True Sine Wave | [5 empty] | Square Wave | [5 empty] | Modified S-Wave
E. ACTUAL TESTING RESULT :
| TESTING CONDITIONS / SCENARIOS | [10 empty] | STANDARDS | [7 empty] | ACTUAL | [5 empty] | REMARKS
Power Flow Convention from the GRID (DU) (Imp or Exp?) | [10 empty] | : | Import or Export
Power Flow Convention from PV RE Plant (Imp or Exp?) | [10 empty] | : | Import or Export
Anti - Islanding Function (Time to Disconnect from Grid) | [10 empty] | : | ≤ 2 Seconds
Time to Disconnect from the GRID during GRID Interruption | [10 empty] | : | Immediately
Time to Reconnect to the GRID once GRID is Energize | [10 empty] | : | Min. of 120 Secs (≥ 120s)
Actual Power Factor @ Connection Point | [10 empty] | : | Minimum of 85% Lagging
Flicker Severity (Terms | [10 empty] | : | 1 Unit (long), 0.8 Unit Short
DC Injection Limits to the Grid @ Connection Point | [10 empty] | : | ≤ 0.5% of Full Load Current
Frequency Level Requirements (Continuous) | [10 empty] | : | 58.2 ≤ Actual Frequency ≤ 61.8
Voltage Level Requirements (Continuous) | [10 empty] | : | 90 ≤ Actual Voltage ≤ 110
Disconnect Switch Installation | [10 empty] | : | 10 Feet from Connection Point
RE System Grounding Present? | [10 empty] | : | Required
F. FINDINGS :
G. RECOMMENDATION :
H. INSTALLER / SUPPLIER INFORMATION
Company Name: | [14 empty] | Installer Name:
Address:
Contact Number: | [14 empty] | Signature:
I. ACCREDITED ELECTRICIAN INFORMATION
Name of Electrician: | [14 empty] | Accreditation Number:
Address:
Contact Number: | [14 empty] | Signature:
We hereby declare that all information supplied herein are true according to the result of Joint Inspection by QE & DU.
| Inspected by: |  |  |  |  | Signature | [5 empty] | Date |  |  |  |  | Confirmed/Witnessed by: | [7 empty] | Signature
1 | [14 empty] | 1
2 | [14 empty] | 2
3 | [14 empty] | 3
4 | [14 empty] | 4
5 | [14 empty] | 5
6 | [14 empty] | 6
DU / EC Representative | [14 empty] | Qualified End-User / Representative

## NMIREF Form 3
NORTHERN SAMAR ELECTRIC COOPERATIVE, INC.
NORSAMELCO
|  |  | Brgy. Magsaysay, Bobon, Northern Samar | [13 empty] | NMIREF Form 3
Date Applied:
NET METERING and INTERCONNECTION of RENEWABLE ENERGY FACILITY (NMIREF) APPLICATION
APPLICANT (Last Name, Given Name, Middle Name)
| TYPE OF MEMBERSHIP : |  |  |  | Single |  | Joint | Juridical |  | CIVIL STATUS: |  | Single |  | Married |  | Widowed |  | Others
| DATE OF BIRTH : | [7 empty] | GENDER : |  |  |  |  | CIVIL STATUS:
SPOUSE (Last Name, Given Name, Middle Name) If Married
LOCATION OF INSTALLATION (House Number, Street, Barangay, Town/City)
| Consumer Contact #: |  |  |  |  | - |  | -
| PAYMENT DETAILS: |  |  | SOA Amount |  |  |  |  | Amount Paid | [5 empty] | Balance
|  |  |  | OR Number |  |  |  |  | Date Paid | [5 empty] | Remarks
APPLICATION AND CONTRACT
Application is hereby made for electric service supplied by NORSAMELCO to be real by me, in accordance with the condition, named in the Coop electric schedule as approved by the NATIONAL ELECTRIFICATION ADMINISTRATION.
THE APPLICANT AGREES AS FOLLOWS:
1. To take electric from the coop a period of one (1) year, and hereafter until the contract shall be cancelled by at least 30 days written notice given by either party or the other.
2. To pay to the Coop monthly within NINE (9) days after the date of the reading of the electric service furnished.
3. To allow representative of the Coop free access to the premises for the purpose of reading, testing, changing and inspecting meters and upon the discontinuance of service for any reasons to remove.
4. That the Coop shall not be responsible for interruption of service due to cause beyond its control and may disconnect the service upon violation of the terms of contract or when the coop has reasonable grounds to believe that the consumer is using electric current in violation of law and cooperative policies.
ACCEPTED BY:
|  | Applicant’s Name in Print and Signature /Date | [8 empty] | Spouse Name in Print and Signature/Date
Owner of Building Signature over Printed Name / Date
The above contract for electric service accepted this _______ day of ______________, 20____.
|  |  | RECOMMENDING APPROVAL: | [8 empty] | APPROVED BY:
|  |  | RAMIL C. MORA | [8 empty] | Engr. HECTOR N. TABILISMA
|  |  | ISD Manager | [8 empty] | Acting General Manager